Essential Objects and Services
Device Object
Analog, Binary, and Multi-State objects
ReadProperty, WriteProperty
WhoIs, I-Am
WhoHas, Ihave
TimeSynchronization
ReinitializeDevice
DeviceCommunicationControl

---
Device Object
Device Instance Number
System_Status
Object_List
MS/TP Properties
  - Max_Master
  - Max_Info_Frames

---
Analog, Binary, Multi-state
Main property is Present_Value, data type is REAL (Analog), active or inactive (Binary), or an integer index (Multi-state).
Common properties Object_Identifier, Object_Name, Object_Type, Status_Flags, Event_State
Additional properties are object specific
Priority Array for Output objects, optional for Value objects.

---
Priority Array
Highest
Priority
1
Manual Life Safety
9
Available
2
Manual Life Safety
10
Available
3
Available
11
Available
4
Available
12
Available
5
Critical Equipment Control
13
Available
6
Minimum On/Off
14
Available
Lowest Priority
7
Available
15
Available
8
Manual Operator
16
Available
Relinquish_Default

---
ReadProperty
Required service for every BACnet device
Used to read the value of a single property in any object.
The return message includes the object and property details along with the value.
Specific error messages are defined in Clause 15.

---
ReadProperty
ReadProperty-Request ::= SEQUENCE {
    objectIdentifier [0] BACnetObjectIdentifier,
    propertyIdentifier [1] BACnetPropertyIdentifier,
    propertyArrayIndex [2] Unsigned OPTIONAL
        --used only with array datatype
        -- if omitted with an array the entire array is referenced
}
ReadProperty-ACK ::= SEQUENCE {
    objectIdentifier [0] BACnetObjectIdentifier,
    propertyIdentifier [1] BACnetPropertyIdentifier,
    propertyArrayIndex [2] Unsigned OPTIONAL,
        --used only with array datatype
        -- if omitted with an array the entire array is referenced
    propertyValue [3] ABSTRACT-SYNTAX.&Type
}

---
WriteProperty
Optional service for devices
Used to write a value to a single object property.
Uses a simple acknowledge - which could be ignored initially when sequencing many writes to improve speed.
Specific error messages are defined in Clause 15.

---
WriteProperty
WriteProperty-Request ::= SEQUENCE {
    objectIdentifier [0] BACnetObjectIdentifier,
    propertyIdentifier [1] BACnetPropertyIdentifier,
    propertyArrayIndex [2] Unsigned OPTIONAL,
        --used only with array datatype
        -- if omitted with an array the entire
        -- array is referenced
    propertyValue [3] ABSTRACT-SYNTAX.&Type,
    priority [4] Unsigned8 (1..16) OPTIONAL
        --used only when property is commandable
}
BACnet-SimpleACK-PDU ::= SEQUENCE {
    pdu-type [0] Unsigned (0..15), -- 2 for this PDU type
    reserved [1] Unsigned (0..15), -- must be set to zero
    invokeID [2] Unsigned (0..255),
    service-ACK-choice [3] BACnetConfirmedServiceChoice
        -- Context-specific tags 0..3 are NOT used in header encoding
}

---
WhoIs, I-Am
Pair used for Device ID to MAC binding
MAC is derived from source address
Routing information is derived from NPDU
I-Am storms, WhoIs ranges
Most common way for Device binding.

---
WhoIs, I-Am
Who-Is-Request ::= SEQUENCE {
    deviceInstanceRangeLowLimit [0] Unsigned (0..4194303) OPTIONAL,
    deviceInstanceRangeHighLimit [1] Unsigned (0..4194303) OPTIONAL
    -- must be used as a pair, see 16.10
}
I-Am-Request ::= SEQUENCE {
    iAmDeviceIdentifier BACnetObjectIdentifier,
    maxAPDULengthAccepted Unsigned,
    segmentationSupported BACnetSegmentation,
    vendorID Unsigned
}

---
WhoHas, I-Have
Pair used for Device ID binding
  - WhoHas Device ID? I-Have Device ID.
  - WhoHas Object ID? I-Have Object ID.
  - WhoHas Object Name? I-Have Object Name.
MAC is derived from source address
Routing information is derived from NPDU

---
WhoHas, I-Have
Who-Has-Request ::= SEQUENCE {
    limits SEQUENCE {
        deviceInstanceRangeLowLimit [0] Unsigned (0..4194303),
        deviceInstanceRangeHighLimit [1] Unsigned (0..4194303)
    } OPTIONAL,
    object CHOICE {
        objectIdentifier [2] BACnetObjectIdentifier,
        objectName [3] CharacterString
    }
}
I-Have-Request ::= SEQUENCE {
    deviceIdentifier BACnetObjectIdentifier,
    objectIdentifier BACnetObjectIdentifier,
    objectName CharacterString
}

---
TimeSynchronization
Local Time Sync
UTC Time Sync
Can be used to update clock on clockless devices.
Usually designate only one device on a network as a time master.

---
TimeSynchronization
TimeSynchronization-Request ::= SEQUENCE {
    time BACnetDateTime
}
UTCTimeSynchronization-Request ::= SEQUENCE {
    time BACnetDateTime
}
BACnetDateTime ::= SEQUENCE {
    date Date,
    time Time
}

---
ReinitializeDevice
Used to cold or warm restart a device
Password optional (in the clear)
Additional passwords can be used to do alternate activities, such as enable a new ROM or go into Bootloader mode.
Also used for Backup/Restore procedure

---
ReinitializeDevice
ReinitializeDevice-Request ::= SEQUENCE {
    reinitializedStateOfDevice [0] ENUMERATED {
        coldstart (0),
        warmstart (1),
        startbackup (2),
        endbackup (3),
        startrestore (4),
        endrestore (5),
        abortrestore (6)
    },
    password [1] CharacterString (SIZE (1..20)) OPTIONAL
}
BACnet-SimpleACK-PDU ::= SEQUENCE {
    pdu-type [0] Unsigned (0..15), -- 2 for this PDU type
    reserved [1] Unsigned (0..15), -- must be set to zero
    invokeID [2] Unsigned (0..255),
    service-ACK-choice [3] BACnetConfirmedServiceChoice
        -- Context-specific tags 0..3 are NOT used in header encoding
}

---
DeviceCommunicationControl
Used to disable device communications
After disabled, device can only respond to
  - DeviceCommunicationControl Enable
  - ReinitializeDevice
  - Power cycle

---
DeviceCommunicationControl
DeviceCommunicationControl-Request ::= SEQUENCE {
        timeDuration [0] Unsigned16 OPTIONAL,
        enable-disable [1] ENUMERATED {
        enable (0),
        disable (1),
        disable-initiation (2)
    },
    password [2] CharacterString (SIZE(1..20)) OPTIONAL
}
BACnet-SimpleACK-PDU ::= SEQUENCE {
    pdu-type [0] Unsigned (0..15), -- 2 for this PDU type
    reserved [1] Unsigned (0..15), -- must be set to zero
    invokeID [2] Unsigned (0..255),
    service-ACK-choice [3] BACnetConfirmedServiceChoice
        -- Context-specific tags 0..3 are NOT used in header encoding
}